## parameters
| version | converged | OPF_converged | name | res_cost
0 | 2.10.1 | FALSE | TRUE |  | 708.3443

## bus
| in_service | max_vm_pu | min_vm_pu | name | type | vn_kv | zone
0 | TRUE | 1.05 | 0.95 | 1 | b | 135 | 1
1 | TRUE | 1.1 | 0.95 | 2 | b | 135 | 1
2 | TRUE | 1.05 | 0.95 | 3 | b | 135 | 1
3 | TRUE | 1.05 | 0.95 | 4 | b | 135 | 1
4 | TRUE | 1.05 | 0.95 | 5 | b | 135 | 1
5 | TRUE | 1.05 | 0.95 | 6 | b | 135 | 1
6 | TRUE | 1.05 | 0.95 | 7 | b | 135 | 1
7 | TRUE | 1.05 | 0.95 | 8 | b | 135 | 1
8 | TRUE | 1.05 | 0.95 | 9 | b | 135 | 1
9 | TRUE | 1.05 | 0.95 | 10 | b | 135 | 3
10 | TRUE | 1.05 | 0.95 | 11 | b | 135 | 1
11 | TRUE | 1.05 | 0.95 | 12 | b | 135 | 2
12 | TRUE | 1.1 | 0.95 | 13 | b | 135 | 2
13 | TRUE | 1.05 | 0.95 | 14 | b | 135 | 2
14 | TRUE | 1.05 | 0.95 | 15 | b | 135 | 2
15 | TRUE | 1.05 | 0.95 | 16 | b | 135 | 2
16 | TRUE | 1.05 | 0.95 | 17 | b | 135 | 2
17 | TRUE | 1.05 | 0.95 | 18 | b | 135 | 2
18 | TRUE | 1.05 | 0.95 | 19 | b | 135 | 2
19 | TRUE | 1.05 | 0.95 | 20 | b | 135 | 2
20 | TRUE | 1.05 | 0.95 | 21 | b | 135 | 3
21 | TRUE | 1.1 | 0.95 | 22 | b | 135 | 3
22 | TRUE | 1.1 | 0.95 | 23 | b | 135 | 2
23 | TRUE | 1.05 | 0.95 | 24 | b | 135 | 3
24 | TRUE | 1.05 | 0.95 | 25 | b | 135 | 3
25 | TRUE | 1.05 | 0.95 | 26 | b | 135 | 3
26 | TRUE | 1.1 | 0.95 | 27 | b | 135 | 3
27 | TRUE | 1.05 | 0.95 | 28 | b | 135 | 1
28 | TRUE | 1.05 | 0.95 | 29 | b | 135 | 3
29 | TRUE | 1.05 | 0.95 | 30 | b | 135 | 3

## load
| bus | const_i_percent | const_z_percent | controllable | in_service | name | q_mvar | scaling | sn_mva | type | p_mw
0 | 1 | 0 | 0 | FALSE | TRUE |  | 12.7 | 1 |  |  | 21.8259
1 | 2 | 0 | 0 | FALSE | TRUE |  | 1.2 | 1 |  |  | 2.508
2 | 3 | 0 | 0 | FALSE | TRUE |  | 1.6 | 1 |  |  | 7.6
3 | 6 | 0 | 0 | FALSE | TRUE |  | 10.9 | 1 |  |  | 22.8
4 | 7 | 0 | 0 | FALSE | TRUE |  | 30 | 1 |  |  | 33.1039
5 | 9 | 0 | 0 | FALSE | TRUE |  | 2 | 1 |  |  | 5.1493
6 | 11 | 0 | 0 | FALSE | TRUE |  | 7.5 | 1 |  |  | 11.2
7 | 13 | 0 | 0 | FALSE | TRUE |  | 1.6 | 1 |  |  | 6.2
8 | 14 | 0 | 0 | FALSE | TRUE |  | 2.5 | 1 |  |  | 9.8204
9 | 15 | 0 | 0 | FALSE | TRUE |  | 1.8 | 1 |  |  | 4.1296
10 | 16 | 0 | 0 | FALSE | TRUE |  | 5.8 | 1 |  |  | 9
11 | 17 | 0 | 0 | FALSE | TRUE |  | 0.9 | 1 |  |  | 3.2
12 | 18 | 0 | 0 | FALSE | TRUE |  | 3.4 | 1 |  |  | 8.5209
13 | 19 | 0 | 0 | FALSE | TRUE |  | 0.7 | 1 |  |  | 2.2
14 | 20 | 0 | 0 | FALSE | TRUE |  | 11.2 | 1 |  |  | 14.9864
15 | 22 | 0 | 0 | FALSE | TRUE |  | 1.6 | 1 |  |  | 2.9778
16 | 23 | 0 | 0 | FALSE | TRUE |  | 6.7 | 1 |  |  | 8.7
17 | 25 | 0 | 0 | FALSE | TRUE |  | 2.3 | 1 |  |  | 4.0294
18 | 28 | 0 | 0 | FALSE | TRUE |  | 0.9 | 1 |  |  | 2.115
19 | 29 | 0 | 0 | FALSE | TRUE |  | 1.9 | 1 |  |  | 10.6

## gen
| bus | controllable | in_service | name | scaling | sn_mva | type | vm_pu | slack | max_p_mw | max_q_mvar | min_q_mvar | slack_weight | p_mw | min_p_mw
0 | 1 | TRUE | TRUE |  | 1 |  |  | 1 | FALSE | 80 | 60 | -20 | 0 | 16 | 16
1 | 21 | TRUE | TRUE |  | 1 |  |  | 1 | FALSE | 50 | 62.5 | -15 | 0 | 10 | 10
2 | 26 | TRUE | TRUE |  | 1 |  |  | 1 | FALSE | 55 | 48.7 | -15 | 0 | 11 | 11
3 | 22 | TRUE | TRUE |  | 1 |  |  | 1 | FALSE | 30 | 40 | -10 | 0 | 6 | 6
4 | 12 | TRUE | TRUE |  | 1 |  |  | 1 | FALSE | 40 | 44.7 | -15 | 0 | 8 | 8

## shunt
| bus | name | q_mvar | p_mw | vn_kv | step | max_step | in_service
0 | 4 |  | -0.19 | 0 | 135 | 1 | 1 | TRUE
1 | 23 |  | -0.04 | 0 | 135 | 1 | 1 | TRUE

## ext_grid
| bus | in_service | name | va_degree | vm_pu | max_p_mw | min_p_mw | max_q_mvar | min_q_mvar | slack_weight
0 | 0 | TRUE |  | 0 | 1 | 80 | 0 | 150 | -20 | 1

## line
| c_nf_per_km | df | from_bus | g_us_per_km | in_service | length_km | max_i_ka | name | parallel | r_ohm_per_km | std_type | to_bus | type | x_ohm_per_km | max_loading_percent
0 | 436.6391 | 1 | 0 | 0 | TRUE | 1 | 0.55597 |  | 1 | 3.645 |  | 1 | ol | 10.935 | 100
1 | 291.0927 | 1 | 0 | 0 | TRUE | 1 | 0.55597 |  | 1 | 9.1125 |  | 2 | ol | 34.6275 | 100
2 | 291.0927 | 1 | 1 | 0 | TRUE | 1 | 0.27798 |  | 1 | 10.935 |  | 3 | ol | 30.9825 | 100
3 | 0 | 1 | 2 | 0 | TRUE | 1 | 0.55597 |  | 1 | 1.8225 |  | 3 | ol | 7.29 | 100
4 | 291.0927 | 1 | 1 | 0 | TRUE | 1 | 0.55597 |  | 1 | 9.1125 |  | 4 | ol | 36.45 | 100
5 | 291.0927 | 1 | 1 | 0 | TRUE | 1 | 0.27798 |  | 1 | 10.935 |  | 5 | ol | 32.805 | 100
6 | 0 | 1 | 3 | 0 | TRUE | 1 | 0.3849 |  | 1 | 1.8225 |  | 5 | ol | 7.29 | 100
7 | 145.5464 | 1 | 4 | 0 | TRUE | 1 | 0.29937 |  | 1 | 9.1125 |  | 6 | ol | 21.87 | 100
8 | 145.5464 | 1 | 5 | 0 | TRUE | 1 | 0.55597 |  | 1 | 5.4675 |  | 6 | ol | 14.58 | 100
9 | 0 | 1 | 5 | 0 | TRUE | 1 | 0.13685 |  | 1 | 1.8225 |  | 7 | ol | 7.29 | 121
10 | 0 | 1 | 5 | 0 | TRUE | 1 | 0.27798 |  | 1 | 0 |  | 8 | ol | 38.2725 | 100
11 | 0 | 1 | 5 | 0 | TRUE | 1 | 0.13685 |  | 1 | 0 |  | 9 | ol | 102.06 | 100
12 | 0 | 1 | 8 | 0 | TRUE | 1 | 0.27798 |  | 1 | 0 |  | 10 | ol | 38.2725 | 100
13 | 0 | 1 | 8 | 0 | TRUE | 1 | 0.27798 |  | 1 | 0 |  | 9 | ol | 20.0475 | 100
14 | 0 | 1 | 3 | 0 | TRUE | 1 | 0.27798 |  | 1 | 0 |  | 11 | ol | 47.385 | 100
15 | 0 | 1 | 11 | 0 | TRUE | 1 | 0.27798 |  | 1 | 0 |  | 12 | ol | 25.515 | 100
16 | 0 | 1 | 11 | 0 | TRUE | 1 | 0.13685 |  | 1 | 21.87 |  | 13 | ol | 47.385 | 100
17 | 0 | 1 | 11 | 0 | TRUE | 1 | 0.13685 |  | 1 | 12.7575 |  | 14 | ol | 23.6925 | 100
18 | 0 | 1 | 11 | 0 | TRUE | 1 | 0.13685 |  | 1 | 16.4025 |  | 15 | ol | 36.45 | 100
19 | 0 | 1 | 13 | 0 | TRUE | 1 | 0.068427 |  | 1 | 40.095 |  | 14 | ol | 36.45 | 100
20 | 0 | 1 | 15 | 0 | TRUE | 1 | 0.068427 |  | 1 | 14.58 |  | 16 | ol | 34.6275 | 100
21 | 0 | 1 | 14 | 0 | TRUE | 1 | 0.068427 |  | 1 | 20.0475 |  | 17 | ol | 40.095 | 100
22 | 0 | 1 | 17 | 0 | TRUE | 1 | 0.068427 |  | 1 | 10.935 |  | 18 | ol | 23.6925 | 100
23 | 0 | 1 | 18 | 0 | TRUE | 1 | 0.13685 |  | 1 | 5.4675 |  | 19 | ol | 12.7575 | 100
24 | 0 | 1 | 9 | 0 | TRUE | 1 | 0.13685 |  | 1 | 16.4025 |  | 19 | ol | 38.2725 | 100
25 | 0 | 1 | 9 | 0 | TRUE | 1 | 0.13685 |  | 1 | 5.4675 |  | 16 | ol | 14.58 | 100
26 | 0 | 1 | 9 | 0 | TRUE | 1 | 0.13685 |  | 1 | 5.4675 |  | 20 | ol | 12.7575 | 100
27 | 0 | 1 | 9 | 0 | TRUE | 1 | 0.13685 |  | 1 | 12.7575 |  | 21 | ol | 27.3375 | 100
28 | 0 | 1 | 20 | 0 | TRUE | 1 | 0.13685 |  | 1 | 1.8225 |  | 21 | ol | 3.645 | 100
29 | 0 | 1 | 14 | 0 | TRUE | 1 | 0.068427 |  | 1 | 18.225 |  | 22 | ol | 36.45 | 100
30 | 0 | 1 | 21 | 0 | TRUE | 1 | 0.068427 |  | 1 | 21.87 |  | 23 | ol | 32.805 | 100
31 | 0 | 1 | 22 | 0 | TRUE | 1 | 0.068427 |  | 1 | 23.6925 |  | 23 | ol | 49.2075 | 100
32 | 0 | 1 | 23 | 0 | TRUE | 1 | 0.068427 |  | 1 | 34.6275 |  | 24 | ol | 60.1425 | 100
33 | 0 | 1 | 24 | 0 | TRUE | 1 | 0.068427 |  | 1 | 45.5625 |  | 25 | ol | 69.255 | 100
34 | 0 | 1 | 24 | 0 | TRUE | 1 | 0.068427 |  | 1 | 20.0475 |  | 26 | ol | 38.2725 | 100
35 | 0 | 1 | 27 | 0 | TRUE | 1 | 0.27798 |  | 1 | 0 |  | 26 | ol | 72.9 | 100
36 | 0 | 1 | 26 | 0 | TRUE | 1 | 0.068427 |  | 1 | 40.095 |  | 28 | ol | 76.545 | 100
37 | 0 | 1 | 26 | 0 | TRUE | 1 | 0.068427 |  | 1 | 58.32 |  | 29 | ol | 109.35 | 100
38 | 0 | 1 | 28 | 0 | TRUE | 1 | 0.068427 |  | 1 | 43.74 |  | 29 | ol | 82.0125 | 100
39 | 291.0927 | 1 | 7 | 0 | TRUE | 1 | 0.13685 |  | 1 | 10.935 |  | 27 | ol | 36.45 | 100
40 | 145.5464 | 1 | 5 | 0 | TRUE | 1 | 0.13685 |  | 1 | 3.645 |  | 27 | ol | 10.935 | 100

## poly_cost
| element | et | cp0_eur | cq0_eur | cq1_eur_per_mvar | cq2_eur_per_mvar2 | cp1_eur_per_mw | cp2_eur_per_mw2
0 | 0 | ext_grid | 0 | 0 | 0 | 0 | 2 | 0.02
1 | 0 | gen | 0 | 0 | 0 | 0 | 1.4 | 0.014
2 | 1 | gen | 0 | 0 | 0 | 0 | 8 | 0.5
3 | 2 | gen | 0 | 0 | 0 | 0 | 1.625 | 0.00417
4 | 3 | gen | 0 | 0 | 0 | 0 | 2.7 | 0.0225
5 | 4 | gen | 0 | 0 | 0 | 0 | 18 | 0.15

## bus_geodata
| x | y | coords
0 | -1.7275 | -3.1893
1 | -0.56202 | -3.3149
10 | 1.0121 | -1.7415
11 | -0.24837 | -5.7012
12 | -1.3515 | -6.3649
13 | -0.13927 | -6.7357
14 | 0.80418 | -6.4263
15 | -0.9243 | -5.4724
16 | 0.22957 | -4.9094
17 | 1.0937 | -7.4732
18 | 1.8575 | -6.8558
19 | 1.4966 | -5.5567
2 | -1.5906 | -4.1442
20 | 1.8818 | -4.6687
21 | 2.4069 | -4.3993
22 | 2.2749 | -6.1619
23 | 3.117 | -5.1466
24 | 3.7246 | -4.0371
25 | 4.8299 | -4.2705
26 | 3.1039 | -2.8673
27 | 1.8534 | -2.8489
28 | 4.0378 | -2.2835
29 | 3.4709 | -1.7453
3 | -0.37269 | -4.2829
4 | -1.0538 | -2.2394
5 | 0.53091 | -3.4333
6 | -0.067379 | -2.3919
7 | 1.0669 | -2.4312
8 | 1.1038 | -3.1875
9 | 1.1627 | -4.2978

## line_std_types
| type | r_ohm_per_km | q_mm2 | x_ohm_per_km | c_nf_per_km | max_i_ka
NAYY 4x150 SE | cs | 0.208 | 150 | 0.08 | 261 | 0.27
70-AL1/11-ST1A 20.0 | ol | 0.4132 | 70 | 0.36 | 9.7 | 0.29
NA2XS2Y 1x70 RM/25 6/10 kV | cs | 0.443 | 70 | 0.123 | 280 | 0.217
N2XS(FL)2Y 1x300 RM/35 64/110 kV | cs | 0.06 | 300 | 0.144 | 144 | 0.588
NA2XS2Y 1x120 RM/25 6/10 kV | cs | 0.253 | 120 | 0.113 | 340 | 0.28
149-AL1/24-ST1A 10.0 | ol | 0.194 | 149 | 0.315 | 11.25 | 0.47
15-AL1/3-ST1A 0.4 | ol | 1.8769 | 16 | 0.35 | 11 | 0.105
NA2XS2Y 1x185 RM/25 6/10 kV | cs | 0.161 | 185 | 0.11 | 406 | 0.358
NA2XS2Y 1x240 RM/25 6/10 kV | cs | 0.122 | 240 | 0.105 | 456 | 0.416
N2XS(FL)2Y 1x240 RM/35 64/110 kV | cs | 0.075 | 240 | 0.149 | 135 | 0.526
NAYY 4x120 SE | cs | 0.225 | 120 | 0.08 | 264 | 0.242
48-AL1/8-ST1A 10.0 | ol | 0.5939 | 48 | 0.35 | 10.1 | 0.21
94-AL1/15-ST1A 10.0 | ol | 0.306 | 94 | 0.33 | 10.75 | 0.35
NA2XS2Y 1x70 RM/25 12/20 kV | cs | 0.443 | 70 | 0.132 | 190 | 0.22
243-AL1/39-ST1A 20.0 | ol | 0.1188 | 243 | 0.32 | 11 | 0.645
NA2XS2Y 1x150 RM/25 6/10 kV | cs | 0.206 | 150 | 0.11 | 360 | 0.315
184-AL1/30-ST1A 110.0 | ol | 0.1571 | 184 | 0.4 | 8.8 | 0.535
149-AL1/24-ST1A 110.0 | ol | 0.194 | 149 | 0.41 | 8.75 | 0.47
NA2XS2Y 1x240 RM/25 12/20 kV | cs | 0.122 | 240 | 0.112 | 304 | 0.421
122-AL1/20-ST1A 20.0 | ol | 0.2376 | 122 | 0.344 | 10.3 | 0.41
48-AL1/8-ST1A 20.0 | ol | 0.5939 | 48 | 0.372 | 9.5 | 0.21
34-AL1/6-ST1A 10.0 | ol | 0.8342 | 34 | 0.36 | 9.7 | 0.17
24-AL1/4-ST1A 0.4 | ol | 1.2012 | 24 | 0.335 | 11.25 | 0.14
184-AL1/30-ST1A 20.0 | ol | 0.1571 | 184 | 0.33 | 10.75 | 0.535
94-AL1/15-ST1A 20.0 | ol | 0.306 | 94 | 0.35 | 10 | 0.35
NAYY 4x50 SE | cs | 0.642 | 50 | 0.083 | 210 | 0.142
490-AL1/64-ST1A 380.0 | ol | 0.059 | 490 | 0.253 | 11 | 0.96
48-AL1/8-ST1A 0.4 | ol | 0.5939 | 48 | 0.3 | 12.2 | 0.21
NA2XS2Y 1x95 RM/25 6/10 kV | cs | 0.313 | 95 | 0.123 | 315 | 0.249
NA2XS2Y 1x120 RM/25 12/20 kV | cs | 0.253 | 120 | 0.119 | 230 | 0.283
34-AL1/6-ST1A 20.0 | ol | 0.8342 | 34 | 0.382 | 9.15 | 0.17
94-AL1/15-ST1A 0.4 | ol | 0.306 | 94 | 0.29 | 13.2 | 0.35
NA2XS2Y 1x185 RM/25 12/20 kV | cs | 0.161 | 185 | 0.117 | 273 | 0.362
NA2XS2Y 1x150 RM/25 12/20 kV | cs | 0.206 | 150 | 0.116 | 250 | 0.319
243-AL1/39-ST1A 110.0 | ol | 0.1188 | 243 | 0.39 | 9 | 0.645
490-AL1/64-ST1A 220.0 | ol | 0.059 | 490 | 0.285 | 10 | 0.96
N2XS(FL)2Y 1x185 RM/35 64/110 kV | cs | 0.099 | 185 | 0.156 | 125 | 0.457
N2XS(FL)2Y 1x120 RM/35 64/110 kV | cs | 0.153 | 120 | 0.166 | 112 | 0.366
NA2XS2Y 1x95 RM/25 12/20 kV | cs | 0.313 | 95 | 0.132 | 216 | 0.252
122-AL1/20-ST1A 10.0 | ol | 0.2376 | 122 | 0.323 | 11.1 | 0.41
149-AL1/24-ST1A 20.0 | ol | 0.194 | 149 | 0.337 | 10.5 | 0.47
70-AL1/11-ST1A 10.0 | ol | 0.4132 | 70 | 0.339 | 10.4 | 0.29
305-AL1/39-ST1A 110.0 | ol | 0.0949 | 305 | 0.38 | 9.2 | 0.74

## trafo_std_types
| shift_degree | vector_group | vn_hv_kv | pfe_kw | i0_percent | vn_lv_kv | sn_mva | tap_step_degree | tap_neutral | tap_min | vkr_percent | tap_step_percent | tap_side | tap_phase_shifter | tap_max | vk_percent
0.4 MVA 20/0.4 kV | 150 | Dyn5 | 20 | 1.35 | 0.3375 | 0.4 | 0.4 | 0 | 0 | -2 | 1.425 | 2.5 | hv | FALSE | 2 | 6
63 MVA 110/20 kV v1.4.3 and older | 150 | YNd5 | 110 | 33 | 0.086 | 20 | 63 | 0 | 0 | -9 | 0.322 | 1.5 | hv | FALSE | 9 | 11.2
63 MVA 110/10 kV v1.4.3 and older | 150 | YNd5 | 110 | 31.51 | 0.078 | 10 | 63 | 0 | 0 | -9 | 0.31 | 1.5 | hv | FALSE | 9 | 10.04
25 MVA 110/20 kV v1.4.3 and older | 150 | YNd5 | 110 | 29 | 0.071 | 20 | 25 | 0 | 0 | -9 | 0.282 | 1.5 | hv | FALSE | 9 | 11.2
40 MVA 110/20 kV v1.4.3 and older | 150 | YNd5 | 110 | 31 | 0.08 | 20 | 40 | 0 | 0 | -9 | 0.302 | 1.5 | hv | FALSE | 9 | 11.2
0.25 MVA 20/0.4 kV | 150 | Yzn5 | 20 | 0.8 | 0.32 | 0.4 | 0.25 | 0 | 0 | -2 | 1.44 | 2.5 | hv | FALSE | 2 | 6
25 MVA 110/10 kV v1.4.3 and older | 150 | YNd5 | 110 | 28.51 | 0.073 | 10 | 25 | 0 | 0 | -9 | 0.276 | 1.5 | hv | FALSE | 9 | 10.04
0.25 MVA 10/0.4 kV | 150 | Dyn5 | 10 | 0.6 | 0.24 | 0.4 | 0.25 | 0 | 0 | -2 | 1.2 | 2.5 | hv | FALSE | 2 | 4
160 MVA 380/110 kV | 0 | Yy0 | 380 | 60 | 0.06 | 110 | 160 | 0 | 0 | -9 | 0.25 | 1.5 | hv | FALSE | 9 | 12.2
63 MVA 110/10 kV | 150 | YNd5 | 110 | 22 | 0.04 | 10 | 63 | 0 | 0 | -9 | 0.32 | 1.5 | hv | FALSE | 9 | 18
0.63 MVA 20/0.4 kV | 150 | Dyn5 | 20 | 1.65 | 0.2619 | 0.4 | 0.63 | 0 | 0 | -2 | 1.206 | 2.5 | hv | FALSE | 2 | 6
0.4 MVA 10/0.4 kV | 150 | Dyn5 | 10 | 0.95 | 0.2375 | 0.4 | 0.4 | 0 | 0 | -2 | 1.325 | 2.5 | hv | FALSE | 2 | 4
0.63 MVA 10/0.4 kV | 150 | Dyn5 | 10 | 1.18 | 0.1873 | 0.4 | 0.63 | 0 | 0 | -2 | 1.0794 | 2.5 | hv | FALSE | 2 | 4
63 MVA 110/20 kV | 150 | YNd5 | 110 | 22 | 0.04 | 20 | 63 | 0 | 0 | -9 | 0.32 | 1.5 | hv | FALSE | 9 | 18
100 MVA 220/110 kV | 0 | Yy0 | 220 | 55 | 0.06 | 110 | 100 | 0 | 0 | -9 | 0.26 | 1.5 | hv | FALSE | 9 | 12
25 MVA 110/10 kV | 150 | YNd5 | 110 | 14 | 0.07 | 10 | 25 | 0 | 0 | -9 | 0.41 | 1.5 | hv | FALSE | 9 | 12
40 MVA 110/20 kV | 150 | YNd5 | 110 | 18 | 0.05 | 20 | 40 | 0 | 0 | -9 | 0.34 | 1.5 | hv | FALSE | 9 | 16.2
40 MVA 110/10 kV v1.4.3 and older | 150 | YNd5 | 110 | 30.45 | 0.076 | 10 | 40 | 0 | 0 | -9 | 0.295 | 1.5 | hv | FALSE | 9 | 10.04
25 MVA 110/20 kV | 150 | YNd5 | 110 | 14 | 0.07 | 20 | 25 | 0 | 0 | -9 | 0.41 | 1.5 | hv | FALSE | 9 | 12
40 MVA 110/10 kV | 150 | YNd5 | 110 | 18 | 0.05 | 10 | 40 | 0 | 0 | -9 | 0.34 | 1.5 | hv | FALSE | 9 | 16.2

## trafo3w_std_types
| vector_group | vn_mv_kv | vn_lv_kv | shift_lv_degree | shift_mv_degree | pfe_kw | vn_hv_kv | i0_percent | sn_lv_mva | sn_hv_mva | sn_mv_mva | vkr_lv_percent | tap_neutral | tap_min | vk_mv_percent | vkr_hv_percent | vk_lv_percent | tap_max | vkr_mv_percent | tap_step_percent | tap_side | vk_hv_percent
63/25/38 MVA 110/10/10 kV | YN0yn0yn0 | 10 | 10 | 0 | 0 | 35 | 110 | 0.89 | 38 | 63 | 25 | 0.35 | 0 | -10 | 10.4 | 0.28 | 10.4 | 10 | 0.32 | 1.2 | hv | 10.4
63/25/38 MVA 110/20/10 kV | YN0yn0yn0 | 20 | 10 | 0 | 0 | 35 | 110 | 0.89 | 38 | 63 | 25 | 0.35 | 0 | -10 | 10.4 | 0.28 | 10.4 | 10 | 0.32 | 1.2 | hv | 10.4

## res_bus
| vm_pu | va_degree | p_mw | q_mvar | lam_p | lam_q
0 | 1 | 0 | -33.7601 | 19.9984 | 3.3504 | -0.011044
1 | 1.0055 | -0.60034 | -48.4602 | -5.8889 | 3.368 | -4.192e-07
2 | 0.99835 | -2.3718 | 2.508 | 1.2 | 3.4579 | 0.0062548
3 | 0.99866 | -2.8137 | 7.6 | 1.6 | 3.4781 | 0.0089139
4 | 0.99583 | -2.3457 | 0 | -0.18842 | 3.4151 | 0.022667
5 | 0.99402 | -3.1438 | 0 | 0 | 3.4493 | 0.032706
6 | 0.98537 | -3.357 | 22.8 | 10.9 | 3.4678 | 0.042603
7 | 0.98225 | -3.6022 | 33.1039 | 30 | 3.4419 | 0.058281
8 | 1.0162 | -4.4068 | 0 | 0 | 3.7207 | 0.070767
9 | 1.028 | -5.0465 | 5.1493 | 2 | 3.8587 | 0.085474
10 | 1.0162 | -4.4068 | 0 | 0 | 3.7207 | 0.070762
11 | 1.0449 | -5.0283 | 11.2 | 7.5 | 3.7944 | 0.033574
12 | 1.1 | -4.47 | -8 | -43.3028 | 3.7941 | 7.7221e-05
13 | 1.0328 | -5.3879 | 6.2 | 1.6 | 3.9025 | 0.048119
14 | 1.0349 | -4.9873 | 9.8204 | 2.5 | 3.9316 | 0.028769
15 | 1.0305 | -5.3573 | 4.1296 | 1.8 | 3.8468 | 0.069067
16 | 1.0237 | -5.3432 | 9 | 5.8 | 3.8704 | 0.090635
17 | 1.0206 | -5.6638 | 3.2 | 0.9 | 3.9601 | 0.069738
18 | 1.0155 | -5.8794 | 8.5209 | 3.4 | 3.9596 | 0.088037
19 | 1.0178 | -5.7244 | 2.2 | 0.7 | 3.9381 | 0.088928
20 | 1.0379 | -5.2522 | 14.9864 | 11.2 | 3.9417 | 0.027787
21 | 1.0443 | -5.2217 | -10 | -46.6344 | 3.9539 | 9.6561e-06
22 | 1.0471 | -3.136 | -21.8756 | -0.25739 | 3.8184 | -5.1249e-06
23 | 1.0357 | -3.7465 | 8.7 | 6.6571 | 4.2339 | -0.076509
24 | 1.041 | -1.0656 | 0 | 0 | 5.1817 | -0.36017
25 | 1.0226 | -1.5803 | 4.0294 | 2.3 | 5.2722 | -0.30746
26 | 1.0535 | 0.89337 | -47.1376 | -15.6864 | 2.0181 | 7.4953e-09
27 | 1.0004 | -2.9037 | 0 | 0 | 3.2768 | 0.076754
28 | 1.0347 | -0.2299 | 2.115 | 0.9 | 2.0681 | 0.014256
29 | 1.0235 | -1.0671 | 10.6 | 1.9 | 2.1045 | 0.020121

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 13.099 | -14.8776 | -13.0289 | 12.0715 | 0.070109 | -2.8061 | 0.084774 | 0.075548 | 0.084774 | 1 | 0 | 1.0055 | -0.60034 | 15.248
1 | 20.6611 | -5.1208 | -20.4392 | 3.9674 | 0.22193 | -1.1534 | 0.091034 | 0.08919 | 0.091034 | 1 | 0 | 0.99835 | -2.3718 | 16.374
2 | 21.6862 | -4.2002 | -21.4011 | 2.9998 | 0.28516 | -1.2003 | 0.093955 | 0.092544 | 0.093955 | 1.0055 | -0.60034 | 0.99866 | -2.8137 | 33.7988
3 | 17.9312 | -5.1674 | -17.8963 | 5.3072 | 0.034938 | 0.13975 | 0.079938 | 0.079938 | 0.079938 | 0.99835 | -2.3718 | 0.99866 | -2.8137 | 14.3783
4 | 15.5455 | 0.17712 | -15.4253 | -1.6989 | 0.12022 | -1.5217 | 0.066126 | 0.066646 | 0.066646 | 1.0055 | -0.60034 | 0.99583 | -2.3457 | 11.9874
5 | 24.2574 | -2.1597 | -23.9074 | 1.2107 | 0.35001 | -0.949 | 0.10359 | 0.10299 | 0.10359 | 1.0055 | -0.60034 | 0.99402 | -3.1438 | 37.2631
6 | 16.188 | 7.5684 | -16.156 | -7.4403 | 0.032019 | 0.12808 | 0.076526 | 0.076526 | 0.076526 | 0.99866 | -2.8137 | 0.99402 | -3.1438 | 19.8821
7 | 15.4253 | 1.8873 | -15.3025 | -2.5738 | 0.12283 | -0.68652 | 0.066739 | 0.067348 | 0.067348 | 0.99583 | -2.3457 | 0.98537 | -3.357 | 22.497
8 | 7.5339 | 7.4437 | -7.4975 | -8.3262 | 0.036363 | -0.88255 | 0.045566 | 0.048629 | 0.048629 | 0.99402 | -3.1438 | 0.98537 | -3.357 | 8.7467
9 | 25.2836 | 23.0134 | -25.1653 | -22.5402 | 0.1183 | 0.47319 | 0.14709 | 0.14709 | 0.14709 | 0.99402 | -3.1438 | 0.98225 | -3.6022 | 107.4827
10 | 10.6027 | -10.3882 | -10.6027 | 10.8564 | -1.7764e-15 | 0.46828 | 0.063863 | 0.063863 | 0.063863 | 0.99402 | -3.1438 | 1.0162 | -4.4068 | 22.9736
11 | 6.0587 | -5.9361 | -6.0587 | 6.3438 | -8.8818e-16 | 0.40775 | 0.036493 | 0.036493 | 0.036493 | 0.99402 | -3.1438 | 1.028 | -5.0465 | 26.6657
12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0162 | -4.4068 | 1.0162 | -4.4068 | 0
13 | 10.6027 | -10.8564 | -10.6027 | 11.1017 | 1.7764e-15 | 0.24529 | 0.063863 | 0.063863 | 0.063863 | 1.0162 | -4.4068 | 1.028 | -5.0465 | 22.9736
14 | 15.5094 | -17.4754 | -15.5094 | 18.8986 | 3.5527e-15 | 1.4232 | 0.10006 | 0.10006 | 0.10006 | 0.99866 | -2.8137 | 1.0449 | -5.0283 | 35.9947
15 | -8 | -41.0592 | 8 | 43.3028 | 0 | 2.2436 | 0.17121 | 0.17121 | 0.17121 | 1.0449 | -5.0283 | 1.1 | -4.47 | 61.5883
16 | 4.0076 | 3.0388 | -3.9798 | -2.9785 | 0.0278 | 0.060232 | 0.020584 | 0.020584 | 0.020584 | 1.0449 | -5.0283 | 1.0328 | -5.3879 | 15.041
17 | 2.9132 | 6.516 | -2.8806 | -6.4554 | 0.032661 | 0.060656 | 0.029213 | 0.029213 | 0.029213 | 1.0449 | -5.0283 | 1.0349 | -4.9873 | 21.3459
18 | 5.3887 | 5.1057 | -5.3432 | -5.0048 | 0.045422 | 0.10094 | 0.030382 | 0.030382 | 0.030382 | 1.0449 | -5.0283 | 1.0305 | -5.3573 | 22.2004
19 | -2.2202 | 1.3785 | 2.2343 | -1.3657 | 0.014086 | 0.012805 | 0.010821 | 0.010821 | 0.010821 | 1.0328 | -5.3879 | 1.0349 | -4.9873 | 15.8147
20 | 1.2137 | 3.2048 | -1.2048 | -3.1838 | 0.0088463 | 0.02101 | 0.014221 | 0.014221 | 0.014221 | 1.0305 | -5.3573 | 1.0237 | -5.3432 | 20.7833
21 | 7.2399 | 3.1431 | -7.1759 | -3.0152 | 0.063984 | 0.12797 | 0.032617 | 0.032617 | 0.032617 | 1.0349 | -4.9873 | 1.0206 | -5.6638 | 47.6672
22 | 3.9759 | 2.1152 | -3.9643 | -2.0899 | 0.011684 | 0.025314 | 0.018872 | 0.018872 | 0.018872 | 1.0206 | -5.6638 | 1.0155 | -5.8794 | 27.5799
23 | -4.5567 | -1.3101 | 4.5632 | 1.3254 | 0.006539 | 0.015258 | 0.019966 | 0.019966 | 0.019966 | 1.0155 | -5.8794 | 1.0178 | -5.7244 | 14.5896
24 | 6.8065 | 2.1264 | -6.7632 | -2.0254 | 0.043303 | 0.10104 | 0.029665 | 0.029665 | 0.029665 | 1.028 | -5.0465 | 1.0178 | -5.7244 | 21.6765
25 | 7.8145 | 2.6678 | -7.7952 | -2.6162 | 0.019355 | 0.051613 | 0.034351 | 0.034351 | 0.034351 | 1.028 | -5.0465 | 1.0237 | -5.3432 | 25.1007
26 | -0.6236 | -14.2251 | 0.68115 | 14.3594 | 0.057551 | 0.13429 | 0.059234 | 0.059234 | 0.059234 | 1.028 | -5.0465 | 1.0379 | -5.2522 | 43.283
27 | -2.4851 | -10.0148 | 2.5556 | 10.1659 | 0.070522 | 0.15112 | 0.042926 | 0.042926 | 0.042926 | 1.028 | -5.0465 | 1.0443 | -5.2217 | 31.3662
28 | -15.6675 | -25.5595 | 15.7509 | 25.7263 | 0.083431 | 0.16686 | 0.12353 | 0.12353 | 0.12353 | 1.0379 | -5.2522 | 1.0443 | -5.2217 | 90.2636
29 | -16.4139 | 2.178 | 16.6699 | -1.666 | 0.25599 | 0.51198 | 0.068426 | 0.068426 | 0.068426 | 1.0349 | -4.9873 | 1.0471 | -3.136 | 99.9983
30 | -8.3069 | 10.7434 | 8.5098 | -10.439 | 0.20292 | 0.30437 | 0.055613 | 0.055613 | 0.055613 | 1.0443 | -5.2217 | 1.0357 | -3.7465 | 81.2732
31 | 5.2057 | 1.9234 | -5.1691 | -1.8475 | 0.036518 | 0.075846 | 0.022667 | 0.022667 | 0.022667 | 1.0471 | -3.136 | 1.0357 | -3.7465 | 33.1256
32 | -12.0406 | 5.6294 | 12.3535 | -5.0859 | 0.31292 | 0.54349 | 0.054884 | 0.054884 | 0.054884 | 1.0357 | -3.7465 | 1.041 | -1.0656 | 80.2082
33 | 4.0809 | 2.3782 | -4.0294 | -2.3 | 0.051467 | 0.078229 | 0.019404 | 0.019404 | 0.019404 | 1.041 | -1.0656 | 1.0226 | -1.5803 | 28.3578
34 | -16.4344 | 2.7077 | 16.716 | -2.1701 | 0.2816 | 0.5376 | 0.068426 | 0.068426 | 0.068426 | 1.041 | -1.0656 | 1.0535 | 0.89337 | 99.9996
35 | -17.4486 | -12.7081 | 17.4486 | 14.5704 | 0 | 1.8623 | 0.092279 | 0.092279 | 0.092279 | 1.0004 | -2.9037 | 1.0535 | 0.89337 | 33.1958
36 | 5.9519 | 1.6492 | -5.8763 | -1.5049 | 0.075608 | 0.14434 | 0.025071 | 0.025071 | 0.025071 | 1.0535 | 0.89337 | 1.0347 | -0.2299 | 36.6398
37 | 7.021 | 1.6371 | -6.8712 | -1.3561 | 0.14985 | 0.28097 | 0.029266 | 0.029266 | 0.029266 | 1.0535 | 0.89337 | 1.0235 | -1.0671 | 42.7695
38 | 3.7613 | 0.60487 | -3.7288 | -0.54387 | 0.032534 | 0.061001 | 0.015746 | 0.015746 | 0.015746 | 1.0347 | -0.2299 | 1.0235 | -1.0671 | 23.0113
39 | -7.9386 | -7.4598 | 8.004 | 5.7123 | 0.065425 | -1.7475 | 0.04743 | 0.042037 | 0.04743 | 0.98225 | -3.6022 | 1.0004 | -2.9037 | 34.6575
40 | -9.4155 | -7.9031 | 9.4446 | 6.9959 | 0.029056 | -0.90727 | 0.052888 | 0.050245 | 0.052888 | 0.99402 | -3.1438 | 1.0004 | -2.9037 | 38.6459

## res_ext_grid
| p_mw | q_mvar
0 | 33.7601 | -19.9984

## res_load
| p_mw | q_mvar
0 | 21.8259 | 12.7
1 | 2.508 | 1.2
2 | 7.6 | 1.6
3 | 22.8 | 10.9
4 | 33.1039 | 30
5 | 5.1493 | 2
6 | 11.2 | 7.5
7 | 6.2 | 1.6
8 | 9.8204 | 2.5
9 | 4.1296 | 1.8
10 | 9 | 5.8
11 | 3.2 | 0.9
12 | 8.5209 | 3.4
13 | 2.2 | 0.7
14 | 14.9864 | 11.2
15 | 2.9778 | 1.6
16 | 8.7 | 6.7
17 | 4.0294 | 2.3
18 | 2.115 | 0.9
19 | 10.6 | 1.9

## res_shunt
| p_mw | q_mvar | vm_pu
0 | 0 | -0.18842 | 0.99583
1 | 0 | -0.042908 | 1.0357

## res_gen
| p_mw | q_mvar | va_degree | vm_pu
0 | 70.2861 | 18.5889 | -0.60034 | 1.0055
1 | 10 | 46.6344 | -5.2217 | 1.0443
2 | 47.1376 | 15.6864 | 0.89337 | 1.0535
3 | 24.8534 | 1.8574 | -3.136 | 1.0471
4 | 8 | 43.3028 | -4.47 | 1.1

## dtypes
| element | column | dtype
0 | bus | in_service | bool
1 | bus | max_vm_pu | float64
2 | bus | min_vm_pu | float64
3 | bus | name | object
4 | bus | type | object
5 | bus | vn_kv | float64
6 | bus | zone | object
7 | load | bus | uint32
8 | load | const_i_percent | float64
9 | load | const_z_percent | float64
10 | load | controllable | bool
11 | load | in_service | bool
12 | load | name | object
13 | load | q_mvar | float64
14 | load | scaling | float64
15 | load | sn_mva | float64
16 | load | type | object
17 | load | p_mw | float64
18 | gen | bus | uint32
19 | gen | controllable | bool
20 | gen | in_service | bool
21 | gen | name | object
22 | gen | scaling | float64
23 | gen | sn_mva | float64
24 | gen | type | object
25 | gen | vm_pu | float64
26 | gen | slack | bool
27 | gen | max_p_mw | float64
28 | gen | max_q_mvar | float64
29 | gen | min_q_mvar | float64
30 | gen | slack_weight | float64
31 | gen | p_mw | float64
32 | gen | min_p_mw | float64
33 | shunt | bus | uint32
34 | shunt | name | object
35 | shunt | q_mvar | float64
36 | shunt | p_mw | float64
37 | shunt | vn_kv | float64
38 | shunt | step | uint32
39 | shunt | max_step | uint32
40 | shunt | in_service | bool
41 | ext_grid | bus | uint32
42 | ext_grid | in_service | bool
43 | ext_grid | name | object
44 | ext_grid | va_degree | float64
45 | ext_grid | vm_pu | float64
46 | ext_grid | max_p_mw | float64
47 | ext_grid | min_p_mw | float64
48 | ext_grid | max_q_mvar | float64
49 | ext_grid | min_q_mvar | float64
50 | ext_grid | slack_weight | float64
51 | line | c_nf_per_km | float64
52 | line | df | float64
53 | line | from_bus | uint32
54 | line | g_us_per_km | float64
55 | line | in_service | bool
56 | line | length_km | float64
57 | line | max_i_ka | float64
58 | line | name | object
59 | line | parallel | uint32
60 | line | r_ohm_per_km | float64
61 | line | std_type | object
62 | line | to_bus | uint32
63 | line | type | object
64 | line | x_ohm_per_km | float64
65 | line | max_loading_percent | float64
66 | poly_cost | element | uint32
67 | poly_cost | et | object
68 | poly_cost | cp0_eur | float64
69 | poly_cost | cq0_eur | float64
70 | poly_cost | cq1_eur_per_mvar | float64
71 | poly_cost | cq2_eur_per_mvar2 | float64
72 | poly_cost | cp1_eur_per_mw | float64
73 | poly_cost | cp2_eur_per_mw2 | float64
74 | bus_geodata | x | float64
75 | bus_geodata | y | float64
76 | bus_geodata | coords | object
77 | res_bus | vm_pu | float64
78 | res_bus | va_degree | float64
79 | res_bus | p_mw | float64
80 | res_bus | q_mvar | float64
81 | res_bus | lam_p | float64
82 | res_bus | lam_q | float64
83 | res_line | p_from_mw | float64
84 | res_line | q_from_mvar | float64
85 | res_line | p_to_mw | float64
86 | res_line | q_to_mvar | float64
87 | res_line | pl_mw | float64
88 | res_line | ql_mvar | float64
89 | res_line | i_from_ka | float64
90 | res_line | i_to_ka | float64
91 | res_line | i_ka | float64
92 | res_line | vm_from_pu | float64
93 | res_line | va_from_degree | float64
94 | res_line | vm_to_pu | float64
95 | res_line | va_to_degree | float64
96 | res_line | loading_percent | float64
97 | res_ext_grid | p_mw | float64
98 | res_ext_grid | q_mvar | float64
99 | res_load | p_mw | float64
100 | res_load | q_mvar | float64
101 | res_shunt | p_mw | float64
102 | res_shunt | q_mvar | float64
103 | res_shunt | vm_pu | float64
104 | res_gen | p_mw | float64
105 | res_gen | q_mvar | float64
106 | res_gen | va_degree | float64
107 | res_gen | vm_pu | float64